## EDE-Standard
TIMESTAMP | 2014-08-26
#mandatory | mandatory | mandatory | mandatory | mandatory | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional | optional
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | commandable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address
UMG96RM-E | 108 | UMG96RM-E | 8 | 108 | UMG96RM-E | N | N | N | N | Y | N | N | N |  | N
Voltage L1 | 108 | Voltage L1 | 0 | 1 | Spannung effektiv L1 | N | N | N | N | Y | N | N | N | 5 | N
Voltage L2 | 108 | Voltage L2 | 0 | 2 | Spannung effektiv L2 | N | N | N | N | Y | N | N | N | 5 | N
Voltage L3 | 108 | Voltage L3 | 0 | 3 | Spannung effektiv L3 | N | N | N | N | Y | N | N | N | 5 | N
Voltage L2-L1 | 108 | Voltage L2-L1 | 0 | 4 | Spannung effektiv L2-L1 | N | N | N | N | Y | N | N | N | 5 | N
Voltage L3-L2 | 108 | Voltage L3-L2 | 0 | 5 | Spannung effektiv L3-L2 | N | N | N | N | Y | N | N | N | 5 | N
Voltage L1-L3 | 108 | Voltage L1-L3 | 0 | 6 | Spannung effektiv L1-L3 | N | N | N | N | Y | N | N | N | 5 | N
Current L1 | 108 | Current L1 | 0 | 7 | Strom effektiv L1 | N | N | N | N | Y | N | N | N | 3 | N
Current L2 | 108 | Current L2 | 0 | 8 | Strom effektiv L2 | N | N | N | N | Y | N | N | N | 3 | N
Current L3 | 108 | Current L3 | 0 | 9 | Strom effektiv L3 | N | N | N | N | Y | N | N | N | 3 | N
Current L4 | 108 | Current L4 | 0 | 10 | Strom effektiv L4 | N | N | N | N | Y | N | N | N | 3 | N
Current L5 | 108 | Current L5 | 0 | 11 | Strom effektiv L5 | N | N | N | N | Y | N | N | N | 3 | N
Current L6 | 108 | Current L6 | 0 | 12 | Strom effektiv L6 | N | N | N | N | Y | N | N | N | 3 | N
Current Sum L1-L3 | 108 | Current Sum L1-L3 | 0 | 13 | Strom effektiv Summe L1..L3 | N | N | N | N | Y | N | N | N | 3 | N
Frequency | 108 | Frequency | 0 | 14 | Frequenz | N | N | N | N | Y | N | N | N | 27 | N
Active Power L1 | 108 | Active Power L1 | 0 | 15 | Wirkleistung L1 | N | N | N | N | Y | N | N | N | 47 | N
Active Power L2 | 108 | Active Power L2 | 0 | 16 | Wirkleistung L2 | N | N | N | N | Y | N | N | N | 47 | N
Active Power L3 | 108 | Active Power L3 | 0 | 17 | Wirkleistung L3 | N | N | N | N | Y | N | N | N | 47 | N
Active Power Sum L1-L3 | 108 | Active Power Sum L1-L3 | 0 | 18 | Wirkleistung Summe L1..L3 | N | N | N | N | Y | N | N | N | 47 | N
Apparent Power L1 | 108 | Apparent Power L1 | 0 | 19 | Scheinleistung L1 | N | N | N | N | Y | N | N | N | 8 | N
Apparent Power L2 | 108 | Apparent Power L2 | 0 | 20 | Scheinleistung L2 | N | N | N | N | Y | N | N | N | 8 | N
Apparent Power L3 | 108 | Apparent Power L3 | 0 | 21 | Scheinleistung L3 | N | N | N | N | Y | N | N | N | 8 | N
Apparent Power SUM L1-L3 | 108 | Apparent Power SUM L1-L3 | 0 | 22 | Scheinleistung Summe L1..L3 | N | N | N | N | Y | N | N | N | 8 | N
Reactive Power L1 | 108 | Reactive Power L1 | 0 | 23 | Blindleistung Grundschwingung L1 | N | N | N | N | Y | N | N | N | 11 | N
Reactive Power L2 | 108 | Reactive Power L2 | 0 | 24 | Blindleistung Grundschwingung L3 | N | N | N | N | Y | N | N | N | 11 | N
Reactive Power L3 | 108 | Reactive Power L3 | 0 | 25 | Blindleistung Grundschwingung L3 | N | N | N | N | Y | N | N | N | 11 | N
Reactive Power SUM L1-L3 | 108 | Reactive Power SUM L1-L3 | 0 | 26 | Blindleistung Grundschwingung Summe L1..L3 | N | N | N | N | Y | N | N | N | 11 | N
Power factor L1 | 108 | Power factor L1 | 0 | 27 | Leistungsfaktor L1 | N | N | N | N | Y | N | N | N | 15 | N
Power factor L2 | 108 | Power factor L2 | 0 | 28 | Leistungsfaktor L2 | N | N | N | N | Y | N | N | N | 15 | N
Power factor L3 | 108 | Power factor L3 | 0 | 29 | Leistungsfaktor L3 | N | N | N | N | Y | N | N | N | 15 | N
Power factor Sum L1-L3 | 108 | Power factor Sum L1-L3 | 0 | 30 | Leistungsfaktor Summe L1..L3 | N | N | N | N | Y | N | N | N | 15 | N
Active Energy L1 | 108 | Active Energy L1 | 0 | 31 | Wirkarbeit L1 | N | N | N | N | Y | N | N | N | 18 | N
Active Energy L2 | 108 | Active Energy L2 | 0 | 32 | Wirkarbeit L2 | N | N | N | N | Y | N | N | N | 18 | N
Active Energy L3 | 108 | Active Energy L3 | 0 | 33 | Wirkarbeit L3 | N | N | N | N | Y | N | N | N | 18 | N
Active Energy Sum L1-L3 | 108 | Active Energy Sum L1-L3 | 0 | 34 | Wirkarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N | 18 | N
Consumed Active Energy L1 | 108 | Consumed Active Energy L1 | 0 | 35 | Bezogene Wirkarbeit L1 | N | N | N | N | Y | N | N | N | 18 | N
Consumed Active Energy L2 | 108 | Consumed Active Energy L2 | 0 | 36 | Bezogene Wirkarbeit L3 | N | N | N | N | Y | N | N | N | 18 | N
Consumed Active Energy L3 | 108 | Consumed Active Energy L3 | 0 | 37 | Bezogene Wirkarbeit L3 | N | N | N | N | Y | N | N | N | 18 | N
Consumed Active Energy sum L1-L3 | 108 | Consumed Active Energy sum L1-L3 | 0 | 38 | Bezogene Wirkarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N | 18 | N
Supplied Active Energy L1 | 108 | Supplied Active Energy L1 | 0 | 39 | Gelieferte Wirkarbeit L1 | N | N | N | N | Y | N | N | N | 18 | N
Supplied Active Energy L2 | 108 | Supplied Active Energy L2 | 0 | 40 | Gelieferte Wirkarbeit L2 | N | N | N | N | Y | N | N | N | 18 | N
Supplied Active Energy L3 | 108 | Supplied Active Energy L3 | 0 | 41 | Gelieferte Wirkarbeit L3 | N | N | N | N | Y | N | N | N | 18 | N
Supplied Active Energy Sum L1-L3 | 108 | Supplied Active Energy Sum L1-L3 | 0 | 42 | Gelieferte Wirkarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N | 18 | N
Apparent Energy L1 | 108 | Apparent Energy L1 | 0 | 43 | Scheinarbeit L1 | N | N | N | N | Y | N | N | N |  | N
Apparent Energy L2 | 108 | Apparent Energy L2 | 0 | 44 | Scheinarbeit L2 | N | N | N | N | Y | N | N | N |  | N
Apparent Energy L3 | 108 | Apparent Energy L3 | 0 | 45 | Scheinarbeit L3 | N | N | N | N | Y | N | N | N |  | N
Apparent Energy Sum L1-L3 | 108 | Apparent Energy Sum L1-L3 | 0 | 46 | Scheinarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N |  | N
Reactive Energy L1 | 108 | Reactive Energy L1 | 0 | 47 | Blindarbeit L1 | N | N | N | N | Y | N | N | N |  | N
Reactive Energy L2 | 108 | Reactive Energy L2 | 0 | 48 | Blindarbeit L2 | N | N | N | N | Y | N | N | N |  | N
Reactive Energy L3 | 108 | Reactive Energy L3 | 0 | 49 | Blindarbeit L3 | N | N | N | N | Y | N | N | N |  | N
Reactive Energy Sum L1-L3 | 108 | Reactive Energy Sum L1-L3 | 0 | 50 | Blindarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N |  | N
Inductive Reactive Energy L1 | 108 | Inductive Reactive Energy L1 | 0 | 51 | Induktive Blindarbeit L1 | N | N | N | N | Y | N | N | N |  | N
Inductive Reactive Energy L2 | 108 | Inductive Reactive Energy L2 | 0 | 52 | Induktive Blindarbeit L2 | N | N | N | N | Y | N | N | N |  | N
Inductive Reactive Energy L3 | 108 | Inductive Reactive Energy L3 | 0 | 53 | Induktive Blindarbeit L3 | N | N | N | N | Y | N | N | N |  | N
Inductive Reactive Energy Sum L1-L3 | 108 | Inductive Reactive Energy Sum L1-L3 | 0 | 54 | Induktive Blindarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N |  | N
Capacitive Reactive Energy L1 | 108 | Capacitive Reactive Energy L1 | 0 | 55 | Kapazitive Blindarbeit L1 | N | N | N | N | Y | N | N | N |  | N
Capacitive Reactive Energy L2 | 108 | Capacitive Reactive Energy L2 | 0 | 56 | Kapazitive Blindarbeit L2 | N | N | N | N | Y | N | N | N |  | N
Capacitive Reactive Energy L3 | 108 | Capacitive Reactive Energy L3 | 0 | 57 | Kapazitive Blindarbeit L3 | N | N | N | N | Y | N | N | N |  | N
Capacitive Reactive Energy Sum L1-L3 | 108 | Capacitive Reactive Energy Sum L1-L3 | 0 | 58 | Kapazitive Blindarbeit Summe L1..L3 | N | N | N | N | Y | N | N | N |  | N
Temperatur1 | 108 | Temperatur1 | 0 | 59 | Temperatur Extern 1 | N | N | N | N | Y | N | N | N | 62 | N
Temperatur2 | 108 | Temperatur2 | 0 | 60 | Temperatur Extern 2 | N | N | N | N | Y | N | N | N | 62 | N
Digital-Out1 | 108 | Digital-Out1 | 4 | 61 | Zustand Digitalausgang 1 (Klemme 14 Gruppe 1) | N | N | N | N | Y | N | N | N |  | N
Digital-Out2 | 108 | Digital-Out2 | 4 | 62 | Zustand Digitalausgang 2 (Klemme 15 Gruppe 1) | N | N | N | N | Y | N | N | N |  | N
Digital-Out3 | 108 | Digital-Out3 | 4 | 63 | Zustand Digitalausgang 3 (Klemme 29 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Digital-Out4 | 108 | Digital-Out4 | 4 | 64 | Zustand Digitalausgang 4 (Klemme 30 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Digital-Out5 | 108 | Digital-Out5 | 4 | 65 | Zustand Digitalausgang 5 (Klemme 31 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Digital-In3 | 108 | Digital-In3 | 2 | 66 | Zustand Digitaleingang 1 (Klemme 29 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Digital-In4 | 108 | Digital-In4 | 2 | 67 | Zustand Digitaleingang 2 (Klemme 29 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Digital-In5 | 108 | Digital-In5 | 2 | 68 | Zustand Digitaleingang 3 (Klemme 29 Gruppe 2) | N | N | N | N | Y | N | N | N |  | N
Diff1 Alarm | 108 | Diff1 Alarm | 2 | 69 | Differenzstrom Alarm 1 | N | N | N | N | Y | N | N | N |  | N
Diff2 Alarm | 108 | Diff2 Alarm | 2 | 70 | Differenzstrom Alarm 2 | N | N | N | N | Y | N | N | N |  | N
Diff1 Overcurrent | 108 | Diff1 Overcurrent | 2 | 71 | Differenzstrom Überstrom Ereignis 1 | N | N | N | N | Y | N | N | N |  | N
Diff2 Overcurrent | 108 | Diff2 Overcurrent | 2 | 72 | Differenzstrom Überstrom Ereignis 2 | N | N | N | N | Y | N | N | N |  | N
Diff1 Warn | 108 | Diff1 Warn | 2 | 73 | Differenzstrom Warnung 1 | N | N | N | N | Y | N | N | N |  | N
Diff2 Warn | 108 | Diff2 Warn | 2 | 74 | Differenzstrom Warnung 2 | N | N | N | N | Y | N | N | N |  | N
Diff1 Overcurrent Time | 108 | Diff1 Overcurrent Time | 0 | 75 | Differenzstrom Überstrom Ereignis 1 Zeit | N | N | N | N | Y | N | N | N |  | N
Diff2 Overcurrent Time | 108 | Diff2 Overcurrent Time | 0 | 76 | Differenzstrom Überstrom Ereignis 2 Zeit | N | N | N | N | Y | N | N | N |  | N
Diff1 Transformer broken | 108 | Diff1 Transformer broken | 2 | 77 | Verbindung zu Differenzstromwandler 1 unterbrochen | N | N | N | N | Y | N | N | N |  | N
Diff2 Transformer broken | 108 | Diff2 Transformer broken | 2 | 78 | Verbindung zu Differenzstromwandler 2 unterbrochen | N | N | N | N | Y | N | N | N |  | N

## Object-Types
#Encoding of BACnet Object Types
#Code | Object Type
0 | Analog Input
1 | Analog Output
2 | Analog Value
3 | Binary Input
4 | Binary Output
5 | Binary Value
6 | Calendar
7 | Command
8 | Device
9 | Event-Enrollment
10 | File
11 | Group
12 | Loop
13 | Multistate Input
14 | Multistate Output
15 | Notification Class
16 | Program
17 | Schedule
18 | Averaging
19 | Multistate Value
20 | Trend Log
21 | Life Safety Point
22 | Life Safety Zone
23 | Accumulator
24 | Pulse Converter

## Unit-Texts
#Encoding of BACnet Engineering Units
#Code | Unit Text
166 | METERS-PER-SECOND-PER-SECOND
0 | SQUARE-METERS
116 | SQUARE-CENTIMETERS
1 | SQUARE-FEET
115 | SQUARE-INCHES
105 | CURRENCY1
106 | CURRENCY2
107 | CURRENCY3
108 | CURRENCY4
109 | CURRENCY5
110 | CURRENCY6
111 | CURRENCY7
112 | CURRENCY8
113 | CURRENCY9
114 | CURRENCY10
2 | MILLIAMPERES
3 | AMPERES
4 | OHMS
145 | MILLIOHMS
122 | KILOHMS
123 | MEGOHMS
5 | VOLTS
124 | MILLIVOLTS
6 | KILOVOLTS
7 | MEGAVOLTS
8 | VOLT-AMPERES
9 | KILOVOLT-AMPERES
10 | MEGAVOLT-AMPERES
11 | VOLT-AMPERES-REACTIVE
12 | KILOVOLT-AMPERES-REACTIVE
13 | MEGAVOLT-AMPERES-REACTIVE
14 | DEGREES-PHASE
15 | POWER-FACTOR
167 | AMPERES-PER-METER
168 | AMPERES-PER-SQUARE-METER
169 | AMPERES-SQUARE-METERS
170 | FARADS
171 | HENRYS
172 | OHM-METERS
173 | SIEMENS
174 | SIEMENS-PER-METER
175 | TESLAS
176 | VOLTS-PER-DEGREE-KELVIN
177 | VOLTS-PER-METER
178 | WEBERS
16 | JOULES
17 | KILOJOULES
125 | KILOJOULES-PER-KG
126 | MEGAJOULES
18 | WATT-HOURS
19 | KILOWATT-HOURS
146 | MEGAWATT-HOURS
20 | BTUS
147 | KILO-BTUS
148 | MEGA-BTUS
21 | THERMS
22 | TON-HOURS
23 | JOULES-PER-KG-DRY-AIR
149 | KILOJOULES-PER-KG-DRY-AIR
150 | MEGAJOULES-PER-KG-DRY-AIR
24 | BTUS-PER-LB-DRY-AIR
117 | BTUS-PER-POUND
127 | JOULES-PER-DEGREE-KELVIN
151 | KILOJOULES-PER-DEGREE-KELVIN
152 | MEGAJOULES-PER-DEGREE-KELVIN
128 | JOULES-PER-KILOGRAM-DEGREE-KELVIN
153 | NEWTON
25 | CYCLES-PER-HOUR
26 | CYCLES-PER-MINUTE
27 | HERTZ
129 | KILOHERTZ
130 | MEGAHERTZ
131 | PER-HOUR
28 | GRAMS-OF-WATER-PER-KILOGRAM-DRY-AIR
29 | PERCENT-RELATIVE-HUMIDITY
30 | MILLIMETERS
118 | CENTIMETERS
31 | METERS
32 | INCHES
33 | FEET
34 | WATTS-PER-SQUARE-FOOT
35 | WATTS-PER-SQUARE-METER
36 | LUMENS
37 | LUXES
38 | FOOT-CANDLES
179 | CANDELAS
180 | CANDELAS-PER-SQUARE-METER
39 | KILOGRAMS
40 | POUNDS-MASS
41 | TONS
154 | GRAMS-PER-SECOND
155 | GRAMS-PER-MINUTE
42 | KILOGRAMS-PER-SECOND
43 | KILOGRAMS-PER-MINUTE
44 | KILOGRAMS-PER-HOUR
119 | POUNDS-MASS-PER-SECOND
45 | POUNDS-MASS-PER-MINUTE
46 | POUNDS-MASS-PER-HOUR
156 | TONS-PER-HOUR
132 | MILLIWATTS
47 | WATTS
48 | KILOWATTS
49 | MEGAWATTS
50 | BTUS-PER-HOUR
157 | KILO-BTUS-PER-HOUR
51 | HORSEPOWER
52 | TONS-REFRIGERATION
53 | PASCALS
133 | HECTOPASCALS
54 | KILOPASCALS
134 | MILLIBARS
55 | BARS
56 | POUNDS-FORCE-PER-SQUARE-INCH
57 | CENTIMETERS-OF-WATER
58 | INCHES-OF-WATER
59 | MILLIMETERS-OF-MERCURY
60 | CENTIMETERS-OF-MERCURY
61 | INCHES-OF-MERCURY
62 | DEGREES-CELSIUS
63 | DEGREES-KELVIN
64 | DEGREES-FAHRENHEIT
65 | DEGREE-DAYS-CELSIUS
66 | DEGREE-DAYS-FAHRENHEIT
120 | DELTA-DEGREES-FAHRENHEIT
121 | DELTA-DEGREES-KELVIN
181 | DEGREES-KELVIN-PER-HOUR
182 | DEGREES-KELVIN-PER-MINUTE
67 | YEARS
68 | MONTHS
69 | WEEKS
70 | DAYS
71 | HOURS
72 | MINUTES
73 | SECONDS
158 | HUNDREDTHS-SECONDS
159 | MILLISECONDS
160 | NEWTON-METERS
161 | MILLIMETERS-PER-SECOND
162 | MILLIMETERS-PER-MINUTE
74 | METERS-PER-SECOND
163 | METERS-PER-MINUTE
164 | METERS-PER-HOUR
75 | KILOMETERS-PER-HOUR
76 | FEET-PER-SECOND
77 | FEET-PER-MINUTE
78 | MILES-PER-HOUR
79 | CUBIC-FEET
80 | CUBIC-METERS
81 | IMPERIAL-GALLONS
82 | LITERS
83 | US-GALLONS
142 | CUBIC-FEET-PER-SECOND
84 | CUBIC-FEET-PER-MINUTE
85 | CUBIC-METERS-PER-SECOND
165 | CUBIC-METERS-PER-MINUTE
135 | CUBIC-METERS-PER-HOUR
86 | IMPERIAL-GALLONS-PER-MINUTE
87 | LITERS-PER-SECOND
88 | LITERS-PER-MINUTE
136 | LITERS-PER-HOUR
89 | US-GALLONS-PER-MINUTE
90 | DEGREES-ANGULAR
91 | DEGREES-CELSIUS-PER-HOUR
92 | DEGREES-CELSIUS-PER-MINUTE
93 | DEGREES-FAHRENHEIT-PER-HOUR
94 | DEGREES-FAHRENHEIT-PER-MINUTE
137 | KWATT-HOURS-PER-SQUARE-METER
138 | KWATT-HOURS-PER-SQUARE-FOOT
139 | MEGAJOULES-PER-SQUARE-METER
140 | MEGAJOULES-PER-SQUARE-FOOT
95 | NO-UNITS
96 | PARTS-PER-MILLION
97 | PARTS-PER-BILLION
98 | PERCENT
143 | PERCENT-OBSCURATION-PER-FOOT
144 | PERCENT-OBSCURATION-PER-METER
99 | PERCENT-PER-SECOND
100 | PER-MINUTE
101 | PER-SECOND
102 | PSI-PER-DEGREE-FAHRENHEIT
103 | RADIANS
104 | REVOLUTIONS-PER-MINUTE
141 | WATTS-PER-SQUARE-METER-DEGREE-KELVIN
183 | JOULE-SECONDS
184 | RADIANS-PER-SECOND
185 | SQUARE-METERS-PER-NEWTON
186 | KILOGRAMS-PER-CUBIC-METER
187 | NEWTON-SECONDS
188 | NEWTONS-PER-METER
189 | WATTS-PER-SQUARE-METER
190 | WATTS-PER-METER-PER-DEGREE-KELVIN